Mackenzie builders
PHARMASAVE ADDITION

NECB 2020 Part 8 Compliance

Stephen Farrell, P.L. (Eng), CEM

Contents

Project Summary	3

Energy Modelling Description	3

Drawings Used for Energy Modelling	3

Building Envelope Summary	4

Assembly Insulation Summary	4

Thermal Transmittance Summary	5

Door and Fenestration Summary	5

Exterior Lighting Summary	5

Interior Lighting Summary	6

Service Hot Water Equipment Summary	6

HVAC Equipment Summary	6

Energy Use Summary	7

GHG Emissions Summary	7

Effective Thermal Resistance Calculations	8

# Project Summary

| Compliance Path: | NECB 2020 Part 8 – Performance Path |
| --- | --- |
| Address: | 10106 100 St |
| City, Province: | La Crete, AB |
| Climate Zone (HDD): | 7B (6700)1 |
| Modelling Software: | HAP 5.11.0.19 |
| Energy Modelling Consultant: | Acacia Engineering Ltd. |
| Professional of Record: | Stephen Farrell |
| Revision # & Date: | #1 – April 8, 2025 |
| Internal Job # | A-3748-25 |
| Project Exceeds Reference Design in Energy Efficiency? | Yes – See Energy Usage Summary for Detailed Results |

1: Fort Vermillion, AB was used in model as the closest location with climatic data available.

# Energy Modelling Description

The proposed project includes an addition to existing building consisting of three CRUs and mechanical room. Changes to the existing building are not subject to NECB compliance as it was not originally constructed in accordance with NECB 2020.

# Drawings Used for Energy Modelling

| Drawing Type | Consultant | Drawing Revision |
| --- | --- | --- |
| Architectural | Railside Design | February 21, 2025 |
| Mechanical2 | -- | -- |
| Electrical2 | -- | -- |

2: Model was done without mechanical and electrical drawings available. Information on M&E was provided by the client.

# Building Envelope Summary

|  | Reference | Proposed | Difference of Reference from Proposed |
| --- | --- | --- | --- |
| Heated Floor Area (m²): | 674.7 | 674.7 | Equal |
| Semi-Heated Floor Area (m²): | 0.0 | 0.0 | Equal |
| Exterior Wall Area (m²): | 352.8 | 352.8 | Equal |
| Vertical Fenestration Area (m²): | 77.6 | 25.9 | +51.7 |
| FDWR (%): | 22.00% | 7.34% | +14.66% |
| Above-Grade Roof Area (m²): | 674.7 | 674.7 | Equal |
| Roof Area in Contact with ground (m²): | 0.0 | 0.0 | Equal |
| Horizonal Fenestration Area (m²): | 13.5 | 0.0 | +13.5 |
| Skylight to Roof Area Ratio (%): | 2% | 0% | +2% |
| Exposed floor (m²): | 0.0 | 0.0 | Equal |
| Solar Absorptance (Wall/Roof): | 0.7 | 0.7 | Equal |
| Air Leakage (L/m²s @75 Pa): | 1.50 | 1.50 | Equal |
| Heat Loss Coefficient (W/°K): | 290.4 | 215.5 | +74.9 |
| Normalized Heat Loss Coefficient (W/ m2°K): | 0.430 | 0.319 | +0.111 |

# Assembly Insulation Summary

| Assembly Type | Description | Insulation Nominal R Value (°F.ft2.hr/BTU) |
| --- | --- | --- |
| Exterior wall | 2x8 wood studs with batt insulation in stud cavity | R28 |
| Roof | Blown-in cellulose insulation | R50 |
| Slab on Grade | Uninsulated | -- |
| Foundation | 6” ICF Foundation wall with 2.5” of rigid insulation on both sides | R20 |

# Thermal Transmittance Summary

| Assembly Type | Reference Umetric (W/m2·°K) Rimperial (°F·ft2·hr/BTU) | Proposed3 Umetric (W/m2·°K) Rimperial (°F·ft2·hr/BTU) | Proposed Vs. Reference Better (+) or Worse (-) Rimperial (°F·ft2·hr/BTU)) |
| --- | --- | --- | --- |
| Exterior Wall | Umet. = 0.190 Rimp. = 29.9 | Umet. = 0.261 Rimp. = 21.8 | -R8.1 |
| Roof | Umet. = 0.117 Rimp. = 48.5 | Umet. = 0.111 Rimp. = 51.4 | +R2.9 |
| Slab on Grade4 | Umet. = 0.757 Rimp. = 7.5 | Umet. = 4.526 Rimp. = 1.3 | -R6.2 |

3: See effective thermal resistance calculations for more details.

4: Slab insulation of the reference building extends 1.2 m around the perimeter.

# Door and Fenestration Summary

| Window Type | Description | Reference Umetric (W/m2·°k) Rimperial (°F·ft2·hr/BTU) | Proposed Umetric (W/m2·°k) Rimperial (°F·ft2·hr/BTU) | Proposed Vs. Reference Better (+) or Worse (-) Rimperial (°F·ft2·hr/BTU) |
| --- | --- | --- | --- | --- |
| Windows | Aluminum frame; clear double glazing | Umet. = 1.44 Rimp. = 3.9 SHGC = PROP | Umet. = 2.725 Rimp. = 2.1 SHGC = 0.765 | -R1.8 |
| Skylights | N/A | Umet. = 2.01 Rimp. = 2.8 SHGC = PROP | N/A | N/A |
| Entrance Doors | Aluminum frame; clear double glazing | Umet. = 1.9 Rimp. = 3 SHGC = PROP | Umet. = 2.725 Rimp. = 2.1 SHGC = 0.765 | -R0.9 |
| Opaque Doors | Insulated metal door | Umet. = 1.9 Rimp. = 3 | Umet. = 0.81 Rimp. = 7 | +R4 |

5: Fenestration shading of the proposed building is modeled using the adjustment factor of 0.8.

# Exterior Lighting Summary

|  | Reference (W) | Proposed (W) | Proposed Vs. Reference Better (+) or Worse (-) |
| --- | --- | --- | --- |
| Total Exterior Lighting: | 400 | 166 | +234 W |

# Interior Lighting Summary

| Space Type | Reference7,8 (W/m2) | Proposed7,8 (W/m2) | Proposed Vs. Reference Better (+) or Worse (-) |
| --- | --- | --- | --- |
| Corridors | 4.40 | 7.41 | -3.01 |
| Storage/Files | 2.26 | 4.68 | -2.43 |
| Offices | 5.58 | 6.86 | -1.28 |
| Reception | 5.05 | 6.48 | -1.43 |
| Washrooms | 4.52 | 4.95 | -0.42 |
| Staff Room | 6.30 | 5.22 | +1.08 |
| Treatment | 12.06 | 5.91 | +6.15 |
| Retail area (CRU 3)9 | 9.00 | 9.00 | Equal |
| Elec/Mech Room | 4.19 | 4.83 | -0.65 |

7: Includes reductions where required or supplied for automatic lighting control.

8: Operating schedules as per NECB 2020 Tables A-8.4.3.2.3(2)-A & B.

9: Interior lighting density for CRU 3 was determined using building area method in absence of interior layout information.

# Service Hot Water Equipment Summary

| System | Reference Equipment | Proposed Equipment | Proposed Vs. Reference Better (+) or Worse (-) |
| --- | --- | --- | --- |
| Service Hot Water: | Gas-fired storage type service water heater. 50 Gal UEF=0.63 | Gas-fired storage type service water heater. 50 Gal UEF=0.70 | UEF: +0.07 |

# HVAC Equipment Summary

| System | Reference Equipment10 | Proposed Equipment | Proposed Vs. Reference Better (+) or Worse (-) |
| --- | --- | --- | --- |
| Space Heating (Mech Room): | Electric Baseboard Heaters | Electric Force Flow Heaters | Equal |
| Space Heating and Cooling (CRUs): | Packaged gas-fired rooftop unit with DX coil. Et=80% 15.0 SEER | Packaged gas-fired rooftop unit with DX coil. Et=80% 14.0 SEER | Et: Equal SEER: -1.0 |
| Ventilation (CRUs): | From RTUs, O/A is below limit for heat recovery | From RTUs, no heat recovery | Equal |

10: Reference heating capacities modelled with appropriate oversizing factors.

# Energy Use Summary

| Major Energy Use | Reference Annual Energy Use (kWh/year) | Proposed Annual Energy Use (kWh/year) | Proposed Vs. Reference Better (+) or Worse (-) (kWh/year) |
| --- | --- | --- | --- |
| Space Heating (Electric): | 3,932 | 2,247 | +1,685 |
| Space Heating (Natural Gas): | 182,020 | 196,976 | -14,956 |
| Space Cooling: | 1,253 | 634 | +619 |
| Fans: | 34,865 | 12,568 | +22,297 |
| Service Hot Water (Natural Gas): | 10,531 | 9,470 | +1,061 |
| Interior Lighting: | 18,142 | 17,143 | +999 |
| Exterior Lighting: | 1,168 | 485 | +683 |
| Receptacle Load: | 11,364 | 11,364 | Equal |
| TOTAL ENERGY USE: | 263,275 | 250,887 | +12,388 |
| Total Energy Use Intensity: | 390.2 kWh/year·m² | 371.84 kWh/year·m² | +18.36 kWh/year·m² |
| Thermal Energy Demand Intensity: | 275.6 kWh/year·m² | 295.27 kWh/year·m² | -19.67 kWh/year·m² |

|  | Reference Annual Energy Use (kWh/year) | Proposed Annual Energy Use (kWh/year) | Proposed Vs. Reference Better (+) or Worse (-) (%) |
| --- | --- | --- | --- |
| Electricity | 70,724 | 44,441 | +37.16% |
| Natural Gas | 192,551 | 206,446 | -7.22% |
| TOTAL | 263,275 | 250,887 | +4.71% |

# GHG Emissions Summary

|  | Reference Annual GHG Emissions (tCO₂e/year) | Proposed Annual GHG Emissions (tCO₂e/year) | Proposed Vs. Reference Better (+) or Worse (-) (%) |
| --- | --- | --- | --- |
| Electricity | 38.19 | 24.00 | +37.16% |
| Natural Gas | 36.46 | 39.10 | -7.22% |
| TOTAL | 74.65 | 63.09 | +15.49% |
| GHG Intensity (kgCO₂e/year·m²) | 110.65 | 93.51 | +15.49% |

Emissions factors from “Emission Factors and Reference Values V2.0” May 2024.

Natural Gas – 0.1894 tCO2e/MWh

Electricity – 0.54 tCO2e/MWh

# Effective Thermal Resistance Calculations

Exterior Wall RSI Calculation

| Transmittance Type |  | Quantity | Detail Ref.11 | Transmittance | Heat Flow (W/°K) | % of Total Heat Flow |
| --- | --- | --- | --- | --- | --- | --- |
| Exterior Wall | Clearfield | 326.9 m² | 8.1.2 | 0.220 | 71.9 | 84.3% |
|  | Window Transition | 72.5 m | 8.3.2 | 0.001 | 0.1 | 0.1% |
|  | Roof/Wall Transition | 82.7 m | 8.4.2 | 0.060 | 5.0 | 5.8% |
|  | Corner Transition | 12.8 m | 8.5.1 | 0.035 | 0.4 | 0.5% |
|  | Foundation Transition | 76.0 m | 8.6.3 | 0.104 | 7.9 | 9.3% |
| Exterior Wall U-Value, W/m2K (BTU/hr ft2°F) |  |  |  |  | 0.261 | 0.046 |
| Exterior Wall R-Value, m2K/W (hr ft2 °F/BTU) |  |  |  |  | 3.83 | 21.8 |

11: Thermal Transmittance values were determined using the Building Envelope Thermal Bridging Guide v.1.6.

| Roof RSI Calculation |  |  |  |
| --- | --- | --- | --- |
| Isothermal Assembly Components (Continuous) |  |  |  |
| Description | Thickness of Material (mm) | Thermal Resistance (RSI), (m2·K)/W per mm | Thermal Resistance (RSI), (m2·K)/W for thickness listed |
| Exterior air film for ceiling, floors & walls | - | - | 0.030 |
| Loose-fill insulation: cellulose (CAN/ULC-S703) | 352.2 | 0.0250 | 8.805 |
| Gypsum board | 15.9 | 0.0063 | 0.100 |
| Interior air film - ceiling (heat flow up) | - | - | 0.110 |
|  | Effective RSI (m²·°K/W) |  | 9.05 |
|  | U Value (W/ m²·°K) |  | 0.111 |
|  | R Value (h·ft²·°F/Btu) |  | 51.4 |
| Slab on Grade RSI Calculation |  |  |  |
| Isothermal Assembly Components (Continuous) |  |  |  |
| Description | Thickness of Material (mm) | Thermal Resistance (RSI), (m2·K)/W per mm | Thermal Resistance (RSI), (m2·K)/W for thickness listed |
| Interior air film - floor (heat flow down) | - | - | 0.160 |
| Concrete: normal-density aggregate: sand and gravel or stone aggregate (2 400 kg/m³) | 152.4 | 0.0004 | 0.061 |
|  | Effective RSI (m²·°K/W) |  | 0.22 |
|  | U Value (W/ m²·°K) |  | 4.526 |
|  | R Value (h·ft²·°F/Btu) |  | 1.3 |